产品特点：

- 高可靠性

- 全范围交流输入

- 效率达88%

- 内置主动式PFC功能

- PF>0.95

- 保护功能完善,短路、过流、过压、过温

- 符合环保要求 RoHs.

- 三防漆防护，仅限EPH系列

- 质保3年

应用领域：

- 工业控制

- 清洁能源

- 轨道交通

- 生产制造

- 对尺寸大小、环境要求十分严酷的场合

- 对寿命、可靠性要求很高的场合

ESF-320-24

产品规格书Product specification

制造安全产品驱动绿色世界 Power a Safe and Green world

Excellent卓越Creative创造United协作

Features:

- High Reliability

- Universal   AC input/full rang

- 88% efficiency

- Built-in active PFC , PF> 0.95

- Protections:Short /Overload/Over voltage/Over temperature

- Comply with RoHs

- Conformal coating protection，EPH series only

- 3 years warranty

Application:

- Industrial control

- Clean energy

- Track and traffic

- Production and Manufacturing

- It is very harsh on the size and use environment

- System with high requirements for life and reliability

| 电话TEL 4006659997/0551-62731110 传真FAX+86-551-65324417 转0 | 安徽省合肥市蜀山区淠河路88号No.88 Pihe road P.O BOX 9023-20,Hefei China | http://www.ecu.com.cn http://www.ecupowersupply.com |
| --- | --- | --- |

订购信息：

设计号 Design NO:ECU2.932

设计Designed

王磊

审核Checked

陈虎

批准Approved

张伟东

基本参数Basic Parameter	1

输入特性 Input Characteristics	1

输出特性Output Characteristics	2

环境特性 Environment Characteristics	2

保护功能 Protection Function	3

电气安全Electrical Safety	3

电磁兼容Electromagnetic Compatibility	4

可靠性数据Reliability	5

结构与安装Mechanical Installation	5

附件（装配示意图、产品安装示意图、降额曲线）Appendix(Product assembly、Standard Mounting、Derating curve	6

版本更改记录 Revisions

| 版本 Rev | 日期 Date | 更改说明 Description | 核准 Approved |
| --- | --- | --- | --- |
| A00 | 2018-04-09 | 第一次发行First Issue |  |

基本参数Basic Parameter

| 项目 Item | 单位 UNIT | 规格 Specification | 备注 Notes |
| --- | --- | --- | --- |
| 输入电压 Input Voltage | Vac | 100-240 |  |
| 输出电压 Output Voltage | Vdc | 24 |  |
| 输出电压可调范围 Adjustable range | V | 21.6~26.4 |  |
| 额定输出电流 Rated current | A | 0~13.4 |  |
| 额定功率 Rated power | W | 320 |  |
| 纹波电压 Ripple&noise | mVp-p | 150 |  |

输出纹波噪声测试条件/DC output ripple & noise test conditions

1)示波器须设置在20M赫兹带宽/Oscilloscope should be limited at 20MHz bandwidth;

2)将0.1UF的陶瓷电容和47UF的电解电容并联在线材末端/ Connect 0.1uF ceramic capacitors and 47uF electrolytic capacitors in parallel at the end of the wire;

3)使用300mm的双绞线连接电源和负载/ Connect the load and power supply with a 300mm twisted pair

输入特性 Input Characteristics

| 项目 Item | 单位 UNIT | 最小值 MIN | 额定值 Rated | 最大值 Max | 备注 Notes |
| --- | --- | --- | --- | --- | --- |
| 输入电压 Input Voltage | Vac | 90 | 230 | 264 | 参考输出降额曲线 Refer to output derating curve. |
|  | Vdc | 127 | 310 | 370 |  |
| 最大介电强度 Maximum dielectric strength | Vac |  |  | 300 | 5S最大耐受时间 5S max |
| 输入频率 Input Frequency | Hz | 47~63 |  |  |  |
| 输入电流 Input Current | A | / | / | 2 | 230Vac， Full load |
|  |  |  |  | 4 | 115Vac，Full Load. |
| 输入冲击电流 Inrush Current | A | / | / | 20 | 115Vac, Full Load. cold start. |
|  |  |  |  | 40 | 230Vac, Full Load. cold start. |
| 功率因数 PFC | / | 0.98 | / | / | 115Vac, Full Load. |
|  |  | 0.95 |  |  | 230Vac, Full Load. |
| 空载损耗 No-load loss | W |  |  | 3 | 230Vac |
| 输入保险 Input Fuse | T6.3A/250Vac |  |  |  |  |

输出特性Output Characteristics

| 项目 Item | 单位 Unit | 最小值 Min | 典型值 Typ | 最大值 Max | 备注 Notes |
| --- | --- | --- | --- | --- | --- |
| 效率 Efficiency | % | 85 | 88 | / | 230Vac/50Hz, Full Load. |
| 负载调整率 Load Regulation | % | / | ±1 | / | 230Vac Full~min load |
| 输入电压调整率 Line Regulation | % | / | ±0.5 | / | 100Vac~264Vac Full load |
| 开机延迟时间 Setup Time | s | / | / | 3 | 115Vac Full Load |
|  | s | / | / | 1.5 | 230Vac Full Load |
| 上升时间 Rise Time | ms | / | / | 80 | 输出从10%上升到90%的时间 The output voltages shall rise from 10% to 90% of their output voltage. |
| 保持时间 Hold time | ms | 8 | / | / | 115Vac,Full Load |
| 过冲响应 Overshoot &undershoot Response | % |  |  | ±5 | 开关机时 Power on/off |
| 负载动态 Load dynamic response | % | / | / | ±5 | 设定周期20ms,升降电流0.1A/us,在50%~100%负载Settling time 20ms R/s 0.1A/us load 50%~100%full load |

环境特性 Environment Characteristics

| 项目 ITEM | 单位 UNIT | 最小值 MIN | 典型值 Rated | 最大值MAX | 备注 Notes |
| --- | --- | --- | --- | --- | --- |
| 温度 Temperature | ℃ | -20 | 25 | 70 | 工作温度Operation Temperature； 50℃以上需降额使用，参考降额曲线。 50~70℃ Refer to derating curve. |
|  |  | -40 | 25 | 85 | 贮藏温度Storage Temperature |
| 相对湿度 Humidity | ℃ | 5% | RH | 90% | 工作湿度Operation Humidity |
|  |  | 5% | RH | 95% | 贮藏湿度Storage Humidity |
| 振动 Vibration | / | IEC 60068-2-6, 正弦10-500Hz，2G，位移0.35mm，X、Y、Z轴各60分钟； Sine Wave:10-500Hz， 2G，displacement of 0.35mm; 60 min per axis for all X, Y, Z directions |  |  |  |
| 冲击 Impact | / | IEC60068-2-27,半正弦波：30G，持续18ms，每个方向3次，共6次 Half Sine Wave: 30G for a duration of 18ms, 3 times per direction, 6 times in total |  |  |  |
| 海拔高度 Altitude | M | ≤2000 |  |  |  |
| 冷却方式 Cooling Mode | 内置风扇冷却Forced air cooling by built-in DC fan |  |  |  |  |
| 防护等级 IP level | IP20 |  |  |  |  |

保护功能 Protection Function

| 项目 Item | 技术要求 Requirement | 注释 Notes |
| --- | --- | --- |
| 短路保护 Short Circuit Protection | 电源无损坏 No damage | 自动恢复 automatically Recovers |
| 过流保护 Over current Protection | 105%~140% @ Io | 自动恢复 automatically Recovers |
| 过压保护 Over voltage Protection | 115~150% @ Vo | 关闭输出电压 Shut down O/P voltage. |
| 过温保护 Over Temperature Protection | 95℃±5℃ | 关闭输出电压，温度下降后恢复 Shut down O/P voltage.Recovers automatically after temperature goes down |

电气安全Electrical Safety

| 项目 Item | 测试方法 Test Method | 测试条件 Test Conditions |
| --- | --- | --- |
| 绝缘电压 Withstand voltage | 输入-输出 I/P-O/P | 1500Vac. 60S,≤10mA |
|  | 输入-大地 I/P-FG | 1500Vac. 60S,≤10mA |
|  | 输出-大地 O/P-FG | 500Vac.60S, ≤10mA |
| 绝缘阻抗 Withstand Resistance | 输入-输出 I/P-O/P | 500VDC.≧5MΩ |
|  | 输入-大地 I/P-FG | 500VDC.≧5MΩ |
|  | 输出-大地 O/P-FG | 500VDC.≧5MΩ |
| 泄露电流 Leakage Current | L、N-外壳/L、N-Case | 3.5mA Max |
|  | L、N-PE/L、N-PE | 3.5mA Max |
| 接地阻抗 PE Resistance | PE-外壳/PE-Case | < 0.1Ohm |
| 设计标准 Design standards | UL508 工业控制类 |  |
|  | EN60950-1资讯类 |  |
|  | UL1310 Class2类电源 | / |
|  | EN60335-1家电类 |  |
|  | EN61347-1灯具类 | / |
|  | IEC60601-1医疗类 | / |

电磁兼容Electromagnetic Compatibility

| 项目 Item | 测试方法 Test Method | 测试条件 Test Conditions |
| --- | --- | --- |
| 静电ESD Electrostatic Discharge | IEC 61000-4-2 GB17626-2 | Criteria B)； Air Discharge: 8kV；Contact Discharge: 6kV |
| 射频辐射RS Radiated Field | IEC 61000-4-3 GB17626-3 | Criteria B)； 80MHz-1GHz, 10V/M, 80% modulation (1kHz)； 1.4GHz-2GHz, 10V/M, 80% modulation (1KHz)； 2GHz-2.7GHz, 10V/M, 80% modulation (1KHz) |
| 脉冲杂讯EFT Electrical Fast Transient / Burst | IEC 61000-4-4 GB17626-4 | Criteria B)； ±2kV |
| 雷击 Surge | IEC 61000-4-5 GB17626-5 | Criteria B)； Common Mode3): 1kV；Differential Mode4): 2kV |
| 射频传导 Conducted | IEC 61000-4-6 GB17626-6 | Criteria A1)； 150kHz-80MHz, 10Vrms，80% modulation (1kHz) |
| 电源磁场 Power Frequency Magnetic Fields | IEC 61000-4-8 GB17626-8 | Criteria A1) 1A/Meter（30A/Meter） |
| 电压瞬断 Voltage Dips and Interruptions | IEC 61000-4-11 GB17626-11 | 0% of 100Vac 40% of 100Vac 70% of 100Vac 0% of 100Vac 0% of 240Vac 40% of 240Vac 70% of 240Vac 0% of 240Vac; 0Vac, 20ms 40Vac, 200ms 70Vac, 500ms 0Vac, 5000ms 0Vac, 20ms 96Vac, 200ms 168Vac, 500ms 0Vac, 5000ms; Criteria A) Criteria A) Criteria A) Criteria B) Criteria A) Criteria A) Criteria A) Criteria B). |
| 低能量脉冲 Low Energy Pulse Test (Ring Wave) | IEC 61000-4-12 GB17626-12 | Level 3 Criteria A)； Common Mode3): 2kV；Differential Mode4): 1kV |
| 谐波 Harmonic Current Emission | IEC/EN 61000-3-2 GB17625-1 | Class A |
| 电磁耐受标准 Immunity Generic Standards |  | EN 55024,GB17618资讯类 |
|  |  | EN55014-2家电类 |
|  | /5) | EN60601-1-2医疗类 |
|  | /5) | EN61547灯具类 |
|  |  | EN61000-6-1,EN50082-1,GB/T17799-1轻工业环境 |
|  |  | EN 61000-6-2,EN55082-2,GB/T17799-2工业环境 |
| 传导和辐射通用标准 CE&RE | /5) | GB9254, CISPR 32, EN 55032 ：Class B 资讯类 |
|  | /5) | GB4824, CISPR 11, EN 55011 ：Class B 医疗类 |
|  | /5) | GB17743，EN55015，CISPR15：Class B 灯具类 |
|  | /5) | GB4343-1, CISPR14，EN55014-1：Class B 家电类 |
|  |  | EN 61000-6-3，FCC Title 47, EN55011：ClassA 工控类 |
| 电压波动和闪烁 Voltage Fluctuation and Flicker | IEC/EN 61000-3-3，GB17625.2 |  |
| 通用电源测试标准 Component Power Supply for General | EN 61204-3 |  |

1)标准A：规格界限内正常性能Criteria A: Normal performance within the specification limits

2) 标准B：可自行恢复的临时性退化或功能丧失Criteria B: Temporary degradation or loss of function which is self-recoverable

3) 不对称：共模（线对地）Asymmetrical: Common mode (Line to earth)

4)对称：差模（线对线）Symmetrical: Differential mode (Line to line)

5) ” / ”：不符合项Non-conformance

6) 电源应视为系统内元件的一部分，需结合终端设备进行EMC确认Power should be considered part of the element within the system, to be combined with the terminal device EMC acknowledgment;

可靠性数据Reliability

| 项目 Item | 数据 Data | 测试条件 Test Conditions |
| --- | --- | --- |
| 产品老化 Burn-in | 100% | 230Va，满载, 40℃±5℃，4小时 |
| 平均无故障时间 MTBF | 200000H Min | 230Vac，满载，25℃，MIL HDBK 217F |
|  | / | 230Vac，满载，40℃，MIL HDBK 217F |
| 质保 Warranty period | 3年 | 40℃，230Va，80% Load，24小时工作 |

结构与安装Mechanical Installation

| 项目 Item | 数据 Data | 备注 Note |
| --- | --- | --- |
| 尺寸mm（长宽高） Size | 215 * 115* 30 |  |
| 重量Kg Weight | 1.0 |  |
| 输入端子 Input Terminal | 脚距9.5mm，9位 Pitch=9.5mm, 9pin | 最大扭矩0.5N.M，直插式连接， 硬导线横截面0.2 mm² ... 4 mm² 柔性导线横截面0.2 mm² ... 2.5 mm² 横截面 AWG 24 ... 12 剥线长度10 mm |
|  | 7 PIN---L |  |
|  | 8 PIN---N |  |
|  | 9 PIN---FG |  |
| 输出端子 Output Terminal | 脚距9.5mm，9位 Pitch=9.5mm, 9pin | 最大扭矩0.5N.M，直插式连接， 硬导线横截面0.2 mm² ... 4 mm² 柔性导线横截面0.2 mm² ... 2.5 mm² 横截面 AWG 24 ... 12 剥线长度10 mm |
|  | 1 PIN---V+ |  |
|  | 2 PIN---V+ |  |
|  | 3 PIN---V+ |  |
|  | 4PIN---V- |  |
|  | 5PIN---V- |  |
|  | 6 PIN---V- |  |

附件（装配示意图、产品安装示意图、降额曲线）Appendix(Product assembly、Standard Mounting、Derating curve

- 产品装配示意图Productassembly

说明：

Introductions:

A：客户安装孔，其中螺纹孔处安装螺钉在电源内不超过4mm。

A:Here is the mounting hole for customer,the screw is locked into the power supply section and can not exceed 4mm inwards.

B：建议扭矩:M3.0螺钉<0.75 N·m；M4.0螺钉<0.8 N·m。

B:Suggested tightening torque:M3.0 screw < 0.75 N·m;M4.0 screw < 0.8 N·m.

C：未注明公差±0.3mm。

C:Tolerance unmarked here,generally±0.3mm.

- 产品安装方式Standard Mounting

- 降额曲线Derating curve：