[image: image10.png]%peor

Ambient Temperature





产品规格书
Products Specification

产品名称 Title: 开关电源  Switching Power Supply    
产品型号 Model:            ESG-50-24             
       设计号 Design NO:       ECU2.939.10662           
	日期Date
	2025.6.30

	版本Rev
	A01

	设计Designed
	孙升

	审核Checked
	

	批准Approved
	


地址：安徽省合肥市高新区习友路3366号

ADD：No. 3366XiYou Rd, Hefei, Anhui, 230000
电话：+86-400-665-9997

TEL：+86-400-665-9997

邮箱：sales@ecu.com.cn
E-mail：sales@ecu.com.cn
网址：//www.ecu.com.cn

http://www.ecu.com.cn
版本更改记录Revisions

	版本

Rev
	日期

Date
	更改说明

Description
	核准

Approved

	A00
	2025-03-21
	第一次发行
	

	A01
	2025-06-30
	更新了产品装配示意图
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	


目  录

1.基本参数Basic Parameter
1
2.技术特性Technical Characteristics
1
2-1 输入特性 Input Characteristics
1
2-2 输出特性Output Characteristics
1
2-3 保护功能 Protection Function
2
2-4安规&电磁兼容Safety& EMC
2
2-5可靠性 Reliability
4
3.环境要求 Environment Requirement
5
4.机械规格 Mechanism Specification
5
4-1 产品尺寸 Product Dimension
5
4-2 产品重量 Product Weight
5
4-3 产品装配示意图 Product Assembly
6
4-4 放置示意图Standard Mounting
7
5.降额曲线 Derating Curve
7


1.基本参数Basic Parameter
	输出电压
Output Voltage
	电压调整范围

 Voltage Adjust Range
	噪声+纹波

Noise & Ripple
	最小负载

Min.Load
	最大负载

Max.Load

	24V
	±10%
	150mV
	0A
	2.2A


备注 Note：
1）电源最大持续输出功率50W。

Maxcontinuous output power 50W.
2）输出电压通过可调电阻调节。

Output voltage is regulated by an adjustable resistor.

2.技术特性 Technical Characteristics

2-1 输入特性 Input Characteristics

	项目

Item
	单位

Unit
	最小值

Min
	额定值

Rated
	最大值

Max
	备注

Remark

	输入电压

Input Voltage
	Vac
	90
	230
	264
	最大300Vac ,持续时间5秒。

Maximum 300Vac input,Duration 5S.

	输入频率

Input Frequency
	Hz
	47
	50/60
	63
	

	输入电流

Input Current
	A
	/
	/
	0.8
	230Vac,满载Full Load.

	
	
	
	
	1.3
	115Vac,满载Full Load.

	输入冲击电流

Inrush Current
	A
	/
	/
	30
	115Vac,满载,冷启动Full load,cold start.

	
	
	/
	/
	45
	230Vac,满载,冷启动Full load,cold start.

	空载功耗
No-load power consumption
	W
	
	
	1
	230Vac,空载/No Load.


2-2 输出特性Output Characteristics

	项目

Item
	单位

Unit
	最小值

Min
	额定值

Rated
	最大值

Max
	测试条件

Test Conditions

	输出电流

Output Current 
	A 
	0 
	/
	2.2
	24V输出，参照降额曲线Test@24V output，refer to derating curve

	负载调整率

Load Regulation
	/
	/
	/
	±0.5%
	输入电压范围内测试，参照降额曲线

Test within input voltage range as specified,refer to derating curve

	线性调整率

Line Regulation
	/
	/
	/
	±0.5%
	负载范围内测试，参照降额曲线

Test within load range as specified,refer to derating curve

	电压误差

Voltage Tolerance
	/
	/
	/
	±1%
	参照降额曲线

Refer to derating curve

	输出纹波噪声

DC Output Ripple&Noise
	mVp-p
	/
	/
	150
	参照备注1

Refer to note 1

	效率
EFFICIENCY
	/
	87%
	/
	/
	输入Input：230Vac

输出Output：24V,满载Full load.

	动态负载
Dynamic Load 
	/
	/
	/
	±5%Vout
	输入Input：115/230Vac，50-100%负载load,1A/uS，100-1K Hz

	开机延迟时间
Setup Time
	mS
	/
	/
	1000
	输入Input：115/230Vac,

输出Output：24V,满载Full Load.

	输出上升时间
DC Output Voltage Rise Time
	mS
	/
	/
	50
	输入Input：115/230Vac,

输出Output：24V,满载Full Load.

	输出保持时间
DC Output Hold-up Time
	mS
	10
	/
	/
	输入Input：115Vac,

输出Output：24V,满载Full Load.

	
	mS
	20
	/
	/
	输入Input：230Vac,

输出Output：24V,满载Full Load.

	开关机过冲
Overshoot
	V
	/
	/
	±5%Vout
	输入Input：230Vac


备注Note:

输出纹波噪声测试条件DC output ripple & noise test conditions

a)使用12英寸（300mm）的双绞线将电源连接至负载，同时在负载端并联0.1uF陶瓷电容和47uF电解电容。
Connect 12”（300mm）twisted cables to the load, parallel 0.1uF ceramic and 47uF electrolytic capacitor to the load terminal.
b)示波器须设置在20M赫兹带宽，在负载端进行测试。
    Oscilloscope probe, 20MHz bandwidth-limited, placed across the load terminals.
电源OK指示
电源绿色发光二极管发光时表明电源工作。
Green LEDs emit light to indicate the power supply is working.
2-3 保护功能 Protection Function

	项目

Item
	范围

Range
	注释

Comments

	输出过压保护

Output Over Voltage Protection
	115~180%
	故障移出后,电源自动恢复。

Recovers automatically after fault condition is removed

	过载保护

Over load Protection
	105~150%
	故障移出后,电源自动恢复。

Recovers automatically after fault condition is removed

	输出短路保护

Output Short Circuit Protection
	/
	故障移出后,电源自动恢复。

Recovers automatically after fault condition is removed


2-4安规&电磁兼容Safety& EMC
安规Safety：

设计参照下列标准
GB4943.1
EN62368-1

	项目

Item
	测试方法

Test Method
	测试条件&性能标准
Test Conditions& Performance Criterion

	绝缘耐压
Dielectric strength:(Hi-pot)
	输入-输出 Input To Output
	3000Vac，60S，≤10mA

	
	输入-地 Input To FG
	1500Vac，60S，≤10mA

	
	输出-地 Output To FG
	500Vac，60S，≤10mA

	绝缘阻抗
Isolation Impedance
	输入-输出 Input To Output
	500Vdc，60S，≥100MΩ (室温70%湿度@room temperature，70% RH )

	
	输入-地 Input To FG
	500Vdc，60S，≥100MΩ (室温70%湿度@room temperature，70% RH )

	
	输出-地 Output To FG
	500Vdc，60S，≥100MΩ (室温70%湿度@room temperature，70% RH )

	泄露电流
Leakage current
	/
	240Vac，50Hz，≤3.5mA


电磁兼容EMC：
	项目
Item
	测试标准
Test Standard
	性能标准
Performance Criterion

	传导干扰
Conducted Emission
	EN55032:2015 Class A
	/

	辐射干扰
Radiated Emission
	EN55032:2015 Class A
	/

	电压波动和闪烁抗扰度
Voltage fluctuation&flicker

	EN61000-3-3:2013
Pst: 1.0
Plt: 0.65
Tdt:500ms
 dmax(%):4%
 Dc(%):3.3%
	Criterion A

	静电放电抗扰度
Electrostatic discharge immunity
	IEC61000-4-2
Air Discharge：±8kV
Contact Discharge：±4kV
	Criterion A

	射频电磁场辐射抗扰度
Radiated, Radio frequency electromagnetic field immunity
	IEC61000-4-3
Frequency Range:80MHz-1000MHz
3V/m
	Criterion A

	电快速瞬变脉冲群抗扰度
Electrical fast transient pulse group immunity
	IEC61000-4-4
AC Power Ports:±1kV
Signal Ports and Telecommunication Ports:0.5kV

	Criterion B

	浪涌抗扰度
Surge immunity
	IEC61000-4-5
L – N：±1KV

L – FG：±2KV

N – FG：±2KV
	Criterion A

	射频场感应的传导干扰抗扰度
Conducted interference immunity induced by RF field
	IEC61000-4-6
Frequency Range：0.15MHz-80MHz
3Vms
	Criterion A

	电源频率磁场抗扰度
Power frequency magnetic field immunity
	IEC61000-4-8
1A/m
	Criterion A

	电压暂降短时中断和电压变化抗扰度
Voltage dips Short interruption and voltage change immunity
	IEC61000-4-11
	Voltage Dips 
>95% reduction,0.5 period
	Criterion A

	
	
	Voltage Dips 
30% reduction,25 period
	Criterion B

	
	
	Voltage interruptions 
>95% reduction,250 period
	Criterion B


*注释comments：
Criterion A：在技术规范内性能正常
Normal performance within limits specified
Criterion B：功能或性能暂时降低或丧失，但能自行恢复
Temporary reduction or loss of function or performance, but self-recovery.

2-5可靠性 Reliability

电源老化 Burn-in test

电源在输入 230Vac(50Hz) ,满载,温度40±5℃条件下老化测试.

The power supply is subjected to burn-in test at input 230Vac(50Hz), full load and temperature of 40±5℃.
平均无故障时间MTBF

200k小时 hour（MIL-HDBK-217F, 25℃）
3.环境要求 Environment Requirement

	项目

Item
	单位

Unit
	最小值

Min
	典型值

Rated
	最大值

Max
	备注

Remark

	 温度

Temperature
	℃
	-30
	25
	70
	工作温度Operation Temperature

(-20摄氏度可在输入电压范围内启动，-30摄氏度可在230Vac启动

The power supply can be started at -20℃ within the input voltage range, and be started at -30℃,230Vac)
参照负载降额曲线Refer to derating curve

	
	
	-40
	25
	80
	贮藏温度Storage Temperature

	相对湿度

Humidity
	/
	5%
	RH
	95%
	工作湿度Operation Humidity

无凝露Without Condensation

	
	
	5%
	RH
	95%
	贮藏湿度Storage Humidity

无凝露Without Condensation

	冷却方式

Cooling Mode
	空气自然冷却 Air Cooling

	振动
Vibration
	10~500Hz，5G 10分钟/周期，X、Y、Z轴各60分钟
10~500Hz，5G 10min/ 1cycle,period for 60 min each along X,Y,Z axes

	海拔高度
Altitude
	≤5000m(参照备注1 Refer to Note 1)


备注Note:

:当操作海拔高于2000米（6500ft）时，操作环温需调降5摄氏度/1000米。

When the operating altitude is higher than 2000m(6500ft),the operating ambient temperature should be lowered by 5℃/1000m. 

4机械规格 Mechanism Specification

4-1 产品尺寸 Product Dimension

长99毫米*宽82毫米*高30毫米; L99mm * W82mm * H30mm .

4-2 产品重量 Product Weight

重量Weight：0.23Kg/PCS
4-3 产品装配示意图 Product Assembly

[image: image1.png]20.520.5 55:0.3
0
«
2 ]
= D
w| 5
s I
Il = <
B bl
€ = ©
S <
oo i
R <
e H
3-611 2
BT R K E < 4m
Length of screw in<4mm
261 48.5+0.5
BRET E A < dmm
Length of screw in<4mm & = F
23.5 1.520.5

92.5%0.3





[image: image2.png]90£0.3 9361

BT HE A K <. 5o

Length of screw in<4.5mm

0.3

TRV

74%0.3

14.540.3

EEEEER

82+1

2] ?&% 22| |2
?ﬁ%ﬁﬂ 22| |*

[ 2]
I |l el P
(A2 2202
Pz





[image: image3.png]B

Introductions:

A ARUCHIET M3, 0BET<0. 4 N+
A:Suggested tightening torque:

M4. 0824T<0.6 N+ m.
.0 screw < 0.4 Nem;M4. 0 screw < 0.6 Nem.





4-4放置示意图 Standard Mounting

[image: image4.png]K FEH A HEH B FH C it

Horizontal Vertical A Vertical B Vertical C No mounting this way





降额曲线Derating Curve

[image: image5.png]C Y SEEREI TUAERAT

ECU ELECTRONICS INDUSTRIAL CO.,LTD.




[image: image6.png]C Y SEEREI TUAERAT

ECU ELECTRONICS INDUSTRIAL CO.,LTD.




� EMBED Excel.Sheet.8 \* MERGEFORMAT ���





� EMBED Excel.Sheet.8 \* MERGEFORMAT ���









[image: image7][image: image8][image: image9.png]100%

50%

20%

0%

240 264

200 220

176

Input Voltage(Vac)



[image: image10.png]_1234567890.xls
Sheet4

		





Sheet4

		0.8		0.8

		1		1

		1		1

		1		1

		1		1

		1		1

		1		1

		1		1

		1		1



Input Voltage(Vac)

Load%



Sheet1

		

				1.5		0.8		90

				1.5		1		100

				1.5		1		115

				1.5		1		132

				1.5		1		176

				1.5		1		200

				1.25		1		220

						1		240

						1		264

				1.4		0.8		90

				1.5		1		100

				1.5		1		110

				1.5		1		150

				1.5		1		175

				1.5		1		230

				1.5		1		264





Sheet1

		



连续工作

Input Voltage（47--63Hz）

Load%



Sheet2

		



Input Voltage(Vac)

Load%



Sheet3

		





		






_1234567891.xls
Sheet4

		





Sheet4

		1		1

		1		1

		1		1

		1		1

		1		1

		1		1

		1		1

		0.8		0.8

		0.6		0.6



Ambient Temperature

Load%



Sheet1

		

				1.5		1		-20

				1.5		1		0

				1.5		1		10

				1.5		1		20

				1.5		1		30

				1.5		1		40

				1.25		1		50

						0.8		60

						0.6		70

				1.4		0.8		90

				1.5		1		100

				1.5		1		110

				1.5		1		150

				1.5		1		175

				1.5		1		230

				1.5		1		264





Sheet1

		



连续工作

Input Voltage（47--63Hz）

Load%



Sheet2

		



Ambient Temperature

Load%

OUTPUT DERATING CURVE



Sheet3

		





		






