产品规格书

Products Specification

产品名称 Title:开关电源  Switching Power Supply

产品型号 Model:         ESG-100-24

设计号 Design NO:     ECU2.939.10664

| 日期Date | 2025.9.8 |
| --- | --- |
| 版本Rev | A01 |
| 设计Designed | 王宁 |
| 审核Checked |  |
| 批准Approved |  |

地址：安徽省合肥市高新区习友路3366号

ADD：No. 3366XiYou Rd, Hefei, Anhui, 230000

电话：+86-400-665-9997

TEL：+86-400-665-9997

邮箱：sales@ecu.com.cn

E-mail：sales@ecu.com.cn

网址：//www.ecu.com.cn

http://www.ecu.com.cn

版本更改记录Revisions

| 版本 Rev | 日期 Date | 更改说明 Description | 核准 Approved |
| --- | --- | --- | --- |
| A00 | 2025-03-21 | 第一次发行 |  |
| A01 | 2025-09-08 | 更新产品装配示意图 |  |

目录

1.基本参数Basic Parameter	1

2.技术特性 Technical Characteristics	1

2-1 输入特性 Input Characteristics	1

2-2 输出特性Output Characteristics	1

2-3 保护功能 Protection Function	2

2-4 安规&电磁兼容Safety& EMC	3

2-5 可靠性 Reliability	4

3.环境要求 Environment Requirement	4

4.机械规格 Mechanism Specification	5

4-1 产品尺寸 Product Dimension	5

4-2 产品重量 Product Weight	5

4-3产品装配示意图 Product Assembly	6

4-4放置示意图Standard Mounting	7

5.降额曲线Derating Curve	7

1.基本参数Basic Parameter

| 输出电压 Output Voltage | 电压调整范围 Voltage Regulation Range | 噪声+纹波 Noise & Ripple | 最小负载 Min.Load | 最大负载 Max.Load |
| --- | --- | --- | --- | --- |
| 24V | ±10% | 150mV | 0A | 4.5A |

备注 Note：

1）电源最大持续输出功率100W。

Maxcontinuous output power 100W.

- 输出电压通过可调电阻调节。

Output voltage is regulated by an adjustable resistor .

2.技术特性Technical Characteristics

2-1 输入特性Input Characteristics

| 项目 Item | 单位 Unit | 最小值 Min | 额定值 Rated | 最大值 Max | 备注 Remark |
| --- | --- | --- | --- | --- | --- |
| 输入电压 Input Voltage | Vac | 90 | 230 | 264 | 参考输出降额曲线 Refer to output derating curve. 最大300Vac ,持续时间5秒。 Max 300Vac input, continue 5S. |
| 输入频率 Input Frequency | Hz | 47 | 50 | 63 |  |
| 输入电流 Input Current | A | / | / | 1.4 | 230Vac,满载Full Load. |
|  |  |  |  | 2.2 | 115Vac,满载Full Load. |
| 输入冲击电流 Inrush Current | A | / | / | 30 | 115Vac,满载,冷启动Full load,cold start. |
|  |  | / | / | 50 | 230Vac,满载,冷启动Full load,cold start. |
| 空载功耗 No-load power consumption | W |  |  | 1.0 | 230Vac,空载/No Load. |

2-2 输出特性Output Characteristics

| 项目 Item | 单位 Unit | 最小值 Min | 额定值 Rated | 最大值 Max | 测试条件 Test Conditions |
| --- | --- | --- | --- | --- | --- |
| 输出电流 Output Current | A | 0 | / | 4.5 | 24V输出，参照降额曲线Test@24V output，refer to derating curve |
| 负载调整率 Load Regulation | / | / | / | ±0.5% | 输入电压范围内测试，参照降额曲线 Test within input voltage range specified,refer to derating curve |
| 线性调整率 Line Regulation | / | / | / | ±0.5% | 负载范围内测试，参照降额曲线 Test within load range specified,refer to derating curve |
| 输出纹波噪声 DC Output Ripple&Noise | mVp-p | / | / | 150 | 参照备注1 Refer to Note 1 |
| 效率 Efficiency | / | 87% | / | / | 输入Input：230Vac 输出Output：24Vdc,满载Full load. |
| 动态负载 Dynamic Load | / | / | / | ±5%Vout | 输入Input：115/230Vac，50-100%负载load,1A/uS，50-10K Hz |
| 开机延迟时间 Setup Time | mS | / | / | 1000 | 输入Input：115/230Vac, 输出Output：24Vdc,满载Full Load. |
| 输出上升时间 DC Output Voltage Rise Time | mS | / | / | 50 | 输入Input：115/230Vac, 输出Output：24Vdc,满载Full Load. |
| 输出保持时间 DC Output Hold-up Time | mS | 10 | / | / | 输入Input：115Vac, 输出Output：24Vdc,满载Full Load. |
|  | mS | 20 | / | / | 输入Input：230Vac, 输出Output：24Vdc,满载Full Load. |
| 开关机过冲 Overshoot | V | / | / | ±5%Vout | 输入Input：115/230Vac |

备注Note:

- 输出纹波噪声测试条件DC output ripple & noise test conditions

a)使用12英寸（300mm）的双绞线将电源连接至负载，同时在负载端并联0.1uF陶瓷电容和47uF电解电容。

Connect 12”（300mm）twisted cables to the load, parallel 0.1uF ceramic and 47uF electrolytic capacitor to the load terminal.

b)示波器须设置在20M赫兹带宽，在负载端进行测试。

Oscilloscope probe, 20MHz bandwidth-limited, placed across the load terminals.

2)电源OK指示

电源绿色发光二极管发光时表明电源工作。

Green LEDs emit light to indicate the power supply is working.

2-3 保护功能 Protection Function

| 项目 Item | 范围 Range | 注释 Comments |
| --- | --- | --- |
| 输出过压保护 Output Over Voltage Protection | 115~180% | 故障移出后,电源自动恢复。 Recovers automatically after fault condition is removed. |
| 过载保护 Over load Protection | 105~150% | 故障移出后,电源自动恢复。 Recovers automatically after fault condition is removed. |
| 输出短路保护 Output Short Circuit Protection | / | 故障移出后,电源自动恢复。 Recovers automatically after fault condition is removed. |

2-4安规&电磁兼容Safety& EMC

安规Safety：

设计参照下列标准Design refers to the following standards:

GB4943.1

EN62368-1

| 项目 Item | 测试方法 Test Method | 测试条件&性能标准 Test Conditions& Performance Standards |
| --- | --- | --- |
| 绝缘耐压 Dielectric strength:(Hi-pot) | 输入-输出 Input to Output | 3000Vac，60S，≤10mA |
|  | 输入-地 Input to FG | 1500Vac，60S，≤10mA |
|  | 输出-地 Output to FG | 500Vac，60S，≤10mA |
| 绝缘阻抗 Isolation Impedance | 输入-输出 Input to Output | 500Vdc，60S，≥100MΩ (室温70%湿度@room temperature，70% RH ) |
|  | 输入-地 Input to FG | 500Vdc，60S，≥100MΩ (室温70%湿度@room temperature，70% RH ) |
|  | 输出-地 Output to FG | 500Vdc，60S，≥100MΩ (室温70%湿度@room temperature，70% RH ) |
| 泄露电流 Leakage current | / | 240Vac，50Hz，≤3.5mA |

电磁兼容EMC：

| 项目 Item | 测试标准 Test Standard |  | 性能标准 Performance Criterion |
| --- | --- | --- | --- |
| 传导干扰 Conducted Emission | EN55032:2015 Class A |  | / |
| 辐射干扰 Radiated Emission | EN55032:2015 Class A |  | / |
| 电压波动和闪烁抗扰度 Voltage fluctuation & Flicker immunity | EN61000-3-3:2013 Pst: 1.0 Plt: 0.65 Tdt:500ms dmax(%):4% Dc(%):3.3% |  | Criterion A |
| 静电放电抗扰度 Electrostatic discharge immunity | IEC61000-4-2 Air Discharge：±8kV Contact Discharge：±4kV |  | Criterion A |
| 射频电磁场辐射抗扰度 Radiated, Radio frequency electromagnetic field immunity | IEC61000-4-3 Frequency Range: 80MHz-1000MHz 3V/m |  | Criterion A |
| 电快速瞬变脉冲群抗扰度 Electrical fast transient pulse group immunity | IEC61000-4-4 AC Power Ports:±1kV Signal Ports and Telecommunication Ports:0.5kV |  | Criterion B |
| 浪涌抗扰度 Surge immunity | IEC61000-4-5 Common Mode: 2kV；Differential Mode: 1kV |  | Criterion A |
| 射频场感应的传导干扰抗扰度 Conducted interference immunity induced by RF field | IEC61000-4-6 Frequency Range：0.15MHz-80MHz 3Vms |  | Criterion A |
| 电源频率磁场抗扰度 Power frequency magnetic field immunity | IEC61000-4-8 1A/m |  | Criterion A |
| 电压暂降短时中断和电压变化抗扰度 Voltage dips Short interruption and voltage change immunity | IEC61000-4-11 | Voltage Dips >95% reduction,0.5 period | Criterion A |
|  |  | Voltage Dips 30% reduction,25 period | Criterion B |
|  |  | Voltage interruptions >95% reduction,250 period | Criterion B |

*注释Comments：

Criterion A：在技术规范内性能正常

Normal performancewithin technical specifications.

Criterion B：功能或性能暂时降低或丧失，但能自行恢复

Temporary reduction or loss of function or performance, but self-recovery.

警告：在居住环境中，运行此设备可能会造成无线电干扰

Warning: Operating this device in a residential environment may cause radio interference.

2-5可靠性 Reliability

电源老化 Burn-in test

电源在输入 230Vac(50Hz) ,满载,温度40±5℃条件下老化测试.

The power supply is subjected to burn-in test at input 230Vac(50Hz), full load and temperature of 40±5℃.

平均无故障时间MTBF

200k小时 hour（MIL-HDBK-217F, 25℃）

3.环境要求 Environment Requirement

| 项目 Item | 单位 Unit | 最小值 Min | 典型值 Rated | 最大值 Max | 备注 Remark |
| --- | --- | --- | --- | --- | --- |
| 温度 Temperature | ℃ | -30 | 25 | 70 | 工作温度Operation Temperature (-20摄氏度可在输入电压范围内启动，-30摄氏度可在230Vac启动 The power supply can be started at -20℃ within the input voltage range, and be started at -30℃,230Vac) 参照负载降额曲线Refer to derating curve |
|  |  | -40 | 25 | 80 | 贮藏温度Storage Temperature |
| 相对湿度 Relative humidity | / | 5% | RH | 95% | 工作湿度Operation Humidity 无凝露 Without Condensation |
|  |  | 5% | RH | 95% | 贮藏湿度Storage Humidity 无凝露 Without Condensation |
| 冷却方式 Cooling Mode | 空气自然冷却 Air Cooling |  |  |  |  |
| 振动 Vibration | 10~500Hz，5G 10分钟/周期，X、Y、Z轴各60分钟 10~500Hz，5G 10min/ 1cycle,period for 60 min each along X,Y,Z axes |  |  |  |  |
| 海拔高度 Altitude | ≤5000m(参照备注1 Refer to Note 1) |  |  |  |  |

备注Note:

- :当操作海拔高于2000米（6500ft）时，操作环温需调降5摄氏度/1000米。

- :When the operating altitude is higher than 2000m(6500ft),the operating ambient

- temperature should be lowered by 5℃/1000m.

4机械规格 Mechanism Specification

4-1 产品尺寸 Product Dimension

长129毫米*宽97.5毫米*高30毫米; L129mm * W97.5mm * H30mm .

4-2 产品重量 Product Weight

重量Weight：0.3Kg/PCS

4-3产品装配示意图 Product Assembly

4-4放置示意图Standard Mounting

- 降额曲线Derating Curve